Absolutely. I’ll keep the exact slide sequence in your current presentation and build the speaking script around it. I won’t rearrange or change the order.

I reviewed the uploaded version, including the sequence from the incident report through networking fundamentals, SCADA architecture, infrastructure, topologies, encapsulation, diagnostics, VLANs, Wireshark, and the final takeaway.

The goal below is to make you sound like you are explaining something you understand from practical SCADA work, rather than reading the text on each slide.

Presentation Script — Exact Order of Your PPT

Slide 1 — Title / Opening

Say:

“Good afternoon everyone.

Today I want to talk about SCADA communication and, more specifically, how we can understand and troubleshoot communication problems between our field devices and SCADA.

I don't want to make this a purely theoretical networking session.

Instead, I want to look at it from the perspective of something we can actually face during commissioning, testing, or troubleshooting.

So throughout the presentation, I'm going to use one simple example — a temperature value of 78 degrees Celsius — and we'll follow that value through the entire communication path.”

Natural transition

“And that brings me to the situation I want to start with.”

Slide 2 — Internal Incident Report

Your slide starts with:

“The PLC is Healthy. SCADA is Healthy. So Why Can't We See the Data?”

and the 78°C communication-failure scenario.

Say:

“Let's imagine this is an actual plant complaint.

The operator tells us:

‘Bearing temperature is showing communication failure.’

So naturally, the first thing we may suspect is the sensor.

We go to the PLC and check it.

The PLC is showing 78 degrees Celsius.

So the sensor is giving us a value and the PLC is receiving it.

Then we check the SCADA server.

SCADA itself is running normally.

The application is running, the server is running, and there is no obvious system failure.

But the operator still cannot see the value.

So now we have an interesting problem.

The value exists at the PLC, but it doesn't exist where the operator needs it.

So the question becomes:

Where exactly did the communication break?”

Make it interactive

Look at your colleagues and ask:

“If this happened in our project, what would you check first?”

Let them answer.

Then:

“Exactly. We could check the PLC, ping the device, check the SCADA driver, check the firewall, and so on.”

“But instead of checking everything randomly, there is a better way.”

“We follow the data.”

Transition

“Before we follow that 78-degree value, let's first understand what has to be correct for two devices to communicate.”

Slide 3 — Before Networking: What Does One Device Need to Talk to Another?

The slide presents the four questions: WHO, WHERE, WHICH SERVICE, HOW.

Say:

“Before a single byte of useful data reaches SCADA, both devices need to agree on some basic things.

I like to think of it as four simple questions.”

WHO — Identity

“First — Who am I talking to?

At the local network level, devices have MAC addresses.

At the IP level, we normally identify the device using an IP address.

So, for example, if our PLC is 192.168.10.10, SCADA needs to know that this is the device it is supposed to communicate with.”

WHERE — Location

“Second — Where is that device?

This is where subnetting and gateways come into the picture.

If the PLC and SCADA are on the same network, communication can happen locally.

If they are on different networks, we need routing through a gateway.”

WHICH SERVICE — Port

“Third — Which service are we trying to access?

This is where ports become important.

For example, Modbus TCP normally uses port 502, while OPC UA commonly uses port 4840.”

HOW — Protocol

“And finally — How are the two devices going to communicate?

This is the protocol.

Both sides need to understand the same communication language — for example Modbus TCP or OPC UA.”

Practical example

“Let's make this very practical.

Imagine I tell you:

PLC IP is 192.168.10.10.

SCADA is trying to communicate with it using Modbus TCP.

Modbus TCP is using port 502.

Now we have already answered:

Who? The PLC at that IP.

Where? Its network/subnet.

Which service? Port 502.

How? Modbus TCP.

If one of these is wrong, our 78°C value isn't going anywhere.”

Transition

“Now let's actually follow that value.”

Slide 4 — So Where Does SCADA Actually Fit?

Your architecture is:

Sensor → PLC → Protocol → TCP/IP → SCADA Driver → Tag → HMI.

Say:

“This is probably the most important slide for understanding the complete journey.

Let's forget about networking terminology for a moment and just follow our 78 degrees.”

1. Sensor

“First, the temperature sensor measures the bearing temperature.

Let's say it is 78°C.”

2. PLC

“That signal reaches the PLC.

The PLC processes it and stores the value in a register or PLC tag.”

3. Industrial Protocol

“Now SCADA needs to retrieve that value.

The PLC may expose it through Modbus TCP, OPC UA, or another industrial protocol.”

4. TCP/IP

“That communication is then carried through the TCP/IP stack.”

5. Network infrastructure

“The packet travels through the network infrastructure — potentially through a switch, router, or firewall.”

6. SCADA driver

“At the SCADA side, the driver receives the communication and interprets the protocol.”

7. SCADA tag

“The driver maps the value to the appropriate SCADA tag.”

8. HMI

“And finally, the operator sees something like:

Bearing Temperature — 78°C.”

Key point

“Now imagine anything in this chain fails.”

“The sensor can be healthy.”

“The PLC can be healthy.”

“The SCADA application can be healthy.”

“But the operator can still see communication failure.”

“Because the complete communication chain has to work.”

Transition

“So now the question is — who is actually moving this data through the network?”

Slide 5 — Who Moves the Data?

Your slide covers router, switch and firewall.

Say:

“There are a few important devices sitting between our PLC and SCADA.

And each one has a different job.”

Switch

“First, the switch.

If the PLC and SCADA are communicating within the same LAN, the switch is responsible for forwarding the Ethernet traffic.

It primarily works with MAC addresses.”

Practical example

“For example, imagine we have ten PLCs connected to one managed switch.

PLC number 1 sends data to the SCADA server.

The switch knows which port the destination device is connected to and forwards the traffic accordingly.”

Router

“Now suppose our PLC network is different from our SCADA server network.

For example:

PLC network — 192.168.10.x

SCADA network — 192.168.20.x

Now we need something to connect those networks.

That's where the router comes in.”

Firewall

“Then we have the firewall.

The firewall is basically asking:

Who is connecting? Where are they connecting? Which port are they using? And is that traffic allowed?”

Practical example

“So imagine everything is correctly configured, but TCP port 502 is blocked.

The PLC is healthy.

SCADA is healthy.

The cable is connected.

You might even be able to ping the PLC.

But Modbus communication still won't work.”

Strong statement

“So every network device can either allow our data to continue — or stop it.”

Transition

“And another thing that determines how these devices are connected is the network topology.”

Slide 6 — Network Topologies in SCADA

Your slide covers Star, Ring, Bus, Mesh, Tree and Hybrid and their practical advantages/disadvantages.

Opening

“Now let's move from individual devices to the overall network architecture.

The topology tells us how the devices are physically or logically connected.”

Star

“The first one is star topology.

This is very common with Ethernet networks.

Devices such as PLCs, HMIs and drives connect back to a central switch.”

Practical example

“For example, inside a control panel we might have:

PLC,

HMI,

VFD,

engineering laptop,

all connected to one managed switch.”

“It's simple and easy to troubleshoot.

But if that central switch fails, several devices can disappear at the same time.”

Ring

“In a ring topology, devices form a circular path.

The advantage is redundancy.

If one communication link is broken, traffic can potentially travel in the other direction.”

Practical example

“Imagine several hydro plant panels connected through fiber.

If one fiber section is damaged, a redundant ring can keep communication alive through the alternative path.”

Bus

“Bus topology uses a shared backbone.

It was especially common in traditional serial industrial networks.

The advantage is lower cabling requirements, but a failure in the main trunk can affect the entire segment.”

Mesh

“Mesh provides multiple communication paths.

That gives us high redundancy, but the network becomes more complex to design and diagnose.”

Tree

“Tree topology is hierarchical.

We can have a core network, distribution level and then local control networks.”

Hybrid

“And in actual industrial plants, we often don't have one pure topology.

We might have a ring backbone, star connections inside individual panels, and serial bus networks connected through gateways.

That's why hybrid architectures are very common.”

Practical conclusion

“So topology isn't just a diagram for documentation.”

“It directly affects what happens when something fails.”

Transition

“Now we've followed the value through the network. But there is another important question — what exactly is traveling through that network?”

Slide 7 — Encapsulation: 78°C Doesn't Travel Alone

The slide describes the journey from physical process through signal transmission and encapsulation to the operator screen.

Say:

“Now let's come back to our 78°C.

One important thing to understand is that 78°C doesn't travel through the network as just a number with no context.”

Practical example

“Imagine the PLC gives SCADA a raw value of 780.

What does 780 mean?”

“Is it 780°C?”

“Is it 78.0°C?”

“Is it some raw ADC value?”

“We don't know without the engineering information.”

Then:

“The physical process gives us the measurement.

The signal carries that measurement.

Then the SCADA system applies the necessary interpretation — tag information, scaling, units, alarm limits and other metadata.”

Example

“For example, the PLC might store 780 and the SCADA configuration interprets it as 78.0°C.”

“Then SCADA may know:

Tag = Bearing Temperature

Unit = °C

Warning limit = 70°C

High alarm = 80°C.”

“Now the operator doesn't just see the number 780.”

“The operator sees meaningful information:

Bearing Temperature: 78°C.”

Important clarification

“So when we talk about encapsulation here, the main idea is that the measurement is carried together with the information needed to interpret and use it.”

Transition

“Now let's say our PLC is reachable. This is where troubleshooting becomes interesting.”

Slide 8 — Diagnostic Workflow: Ping Succeeds, TCP Fails

Your slide specifically covers the difference between successful ping and TCP-level failure.

Opening

“This is one of the most common troubleshooting situations.”

“Someone says:

‘I can ping the PLC, so the network is okay.’”

Pause.

“My response would be:

‘The IP connectivity is working. But we're not finished yet.’”

Practical scenario

“Let's say:

PLC = 192.168.10.10

We ping it.”

“We get a reply.”

“Good.”

“But SCADA still says communication failure.”

“Now we need to test the actual application communication.”

Modbus example

“If we're using Modbus TCP, we can test whether port 502 is reachable.”

Then explain:

“If the TCP connection is refused, there may not be a service listening on that port.”

“If the connection times out, traffic could be getting silently dropped — for example by a firewall.”

Practical troubleshooting sequence

“So instead of saying:

‘The PLC is reachable, therefore everything is fine,’

I'd troubleshoot like this:

Step one: Can I reach the IP?

Step two: Can I reach the required port?

Step three: Is the service actually running?

Step four: Is the firewall allowing it?

Step five: Is the SCADA driver configured correctly?”

Very useful line

“Ping tests reachability. It does not test the SCADA application.”

Transition

“And even if the cable is connected and the IP looks correct, there is another issue we need to consider — VLANs.”

Slide 9 — VLANs

Your slide presents Control, HMI/SCADA and Server VLANs and explains VLAN misconfiguration.

Say:

“VLANs are a good example of why physical connectivity and logical connectivity are two different things.”

Practical scenario

“Imagine we're installing a new PLC.

We connect the Ethernet cable.

The switch port LED is ON.

The PLC has an IP address.

But SCADA cannot communicate with it.”

Ask:

“Would we immediately say the cable is faulty?”

Then:

“Not necessarily.”

“The switch port could be assigned to the wrong VLAN.”

Explain your VLAN example

“For example, we might have:

VLAN 10 — Control

PLCs, RTUs and field devices.

VLAN 20 — HMI/SCADA

Operator workstations.

VLAN 30 — Servers

Historian and application servers.”

Practical example

“Suppose our PLC should be in VLAN 10, but the switch port is accidentally configured for another VLAN.

The Ethernet link can still show green.

The PLC can still be powered.

The IP configuration can still look correct.

But the intended communication path may not exist.”

Strong statement

“A link light tells us we have a physical connection. It does not tell us that we have the correct logical connection.”

Transition

“So if configuration checks aren't enough, we need a way to see what is actually happening on the network.”

Slide 10 — Wireshark

The slide covers Ethernet, IP, TCP/UDP and application-layer inspection, including RSTs, missing SYN-ACKs, retransmissions and malformed frames.

Opening

“This is where Wireshark becomes extremely useful.”

“Instead of asking what we think the network is doing, we can actually look at the packets.”

Practical scenario

“Suppose SCADA is trying to connect to a PLC and communication is failing.”

“We can capture the traffic and ask:

Did the PLC receive the connection request?

Did it respond?

Which IP addresses are involved?

Which port is being used?

Are packets being retransmitted?”

Ethernet

“At the Ethernet level, we can look at MAC addresses and ARP.”

IP

“At the IP level, we can verify source and destination IP addresses.”

TCP

“At the TCP level, we can check the connection establishment and look for resets or retransmissions.”

Application

“And then, depending on the protocol, we can inspect the actual application communication.”

Practical example — SYN

“For example, imagine SCADA sends a TCP SYN to the PLC.”

“If we see the SYN but never see a SYN-ACK, that immediately gives us a clue.”

“Something is preventing the connection from being established.”

RST

“If instead we see a TCP RST, the connection is being actively rejected.”

Retransmissions

“If we see a lot of retransmissions, we may be looking at packet loss, congestion or a network-quality problem.”

Strong statement

“Wireshark changes troubleshooting from guessing to evidence.”

Then connect it back:

“Instead of saying, ‘I think the firewall is blocking it,’ we can capture the communication and look for evidence.”

Slide 11 — Transition / Blank or Visual Slide

If this slide is intentionally mostly visual/blank, don't try to force technical explanation into it.

Use it as a pause.

Say:

“So let's come back to our original problem.”

Pause for a second.

“The PLC has 78°C.”

“The operator doesn't see 78°C.”

“We've now looked at the complete path.”

“So rather than treating it as one big SCADA problem, we can break it into smaller sections.”

Then:

“Where is the value?”

“Where should it go?”

“What protocol is carrying it?”

“What network is carrying it?”

“Is the port reachable?”

“Is the traffic allowed?”

“Is the SCADA driver receiving it?”

Transition

“And that brings us to the main takeaway.”

Slide 12 — TAKEAWAY

Your final slide contains the key statement:

“You Don't Need to Memorize Networking. Follow the Data.”

Say slowly:

“So I want to finish with one simple message.”

“You don't need to memorize networking. Follow the data.”

Pause.

“When an operator says:

‘This tag is not updating.’

Don't immediately restart SCADA.

Don't immediately blame the PLC.

Don't immediately blame the network.”

Then:

“Take that one tag and trace it.”

Point mentally through the chain:

“Sensor.”

“PLC.”

“Protocol.”

“IP.”

“Port.”

“Switch.”

“Router.”

“Firewall.”

“VLAN.”

“SCADA Driver.”

“Tag.”

“HMI.”

Then:

“At each point, ask one simple question:

‘Do I still have my data?’”

Pause.

“If yes, move to the next point.”

“If no, we've found the area where we need to investigate.”

Then finish:

“So the idea is not to memorize every networking term.”

“The idea is to understand the journey of the data.”

“Thank you.”

Then click to:

“Questions?”

8. The most important thing: don't read the PPT

For your particular presentation, I would use this technique.

PPT says:

TCP connection timeout → Firewall is silently dropping the SYN packet

Don't say that exact sentence.

Instead say:

“Let's say I can ping the PLC, but when SCADA tries to connect, it just waits and eventually times out. One possibility is that something in between is silently dropping that connection attempt.”

Then point at the slide.

This makes it sound like you are explaining the concept from experience, rather than reading it.

9. Use these spontaneous questions during the presentation

These are excellent for making the session interactive without making it feel like a formal classroom.

After the incident slide:

“What would you check first?”

After the architecture slide:

“At which point in this chain could the data disappear?”

After the infrastructure slide:

“If I can ping the PLC, does that guarantee Modbus is working?”

After VLAN:

“If the switch port LED is green, does that mean SCADA communication must work?”

Before Wireshark:

“How can we prove whether the packet is actually reaching the destination?”

These questions make your colleagues think rather than just listen.

10. Your overall speaking flow

Don't think of this as 12 separate slides.

Think of it as one story:

“We have 78°C.”

↓

“What does a device need to communicate?”

↓

“Where does SCADA fit?”

↓

“Who moves the packet?”

↓

“How is the network physically organized?”

↓

“What exactly is being transmitted?”

↓

“What if ping works but SCADA doesn't?”

↓

“Could VLAN be the problem?”

↓

“How do we prove what's actually happening?”

↓

“Wireshark.”

↓

“Follow the data.”

That is the storyline I would maintain throughout the entire presentation.

And because your actual slide order is already finalized, I would not change the order. I would change only how you speak around each slide so that the deck remains exactly as you prepared it.